INSPECTION REPORT

Repair of Public Market Comfort Rooms at the old perimeter building along Alunan Avenue

Location: Public Market, Koronadal City

Inspected by: Engr. Severino Johnrome E. Usero
Date Inspected: January 20, 2026

Findings:
	1. Sanitary Pipes

- Existing sanitary pipes from the 2nd floor comfort rooms are damaged, cracked and leaking.

- Pipes are exposed, improperly supported and use inappropriate fittings, causing frequent leakage.

- Presence of strong foul odor along pipe routes indicated active leakage and poor venting

2. Pipe Layout and fittings

- Vertical drop use sharp elbows without clean-outs

- Inadequate venting system contributes to odor accumulation.

3. Septic Tank

- Existing septic tank (approx. 2.7m x 5.2 meters, depth unknown) is always full

- Persistent odor remains even after desludging indicating structural failure and insufficient depth.

4. Public Health Risk

- Continuous odor affects vendors and the general public.

Recommendation:

1. Replace all damaged and leaking sanitary pipes from comfort rooms to septic tank.

2. Install proper pipe fittings, clean outs and air vent.

3. Construct new reinforced septic tank.